FACILITY HEALTH SCORE

Comprehensive Facility Assessment Report

Cedar Crest Hospital 123 Medical Drive Inspection Date: 12/01/2026 Inspector: Ibrahim Yusuf

OVERALL FACILITY HEALTH SCORE 🟡 76/100 GOOD

# EXECUTIVE SUMMARY

This comprehensive facility health assessment was conducted on 12/01/2026 at Cedar Crest Hospital. The inspection evaluated 10 critical facility management categories to determine the overall condition and identify areas requiring immediate attention.

Category Performance Overview:

| Category | Score | Status |
| --- | --- | --- |
| Generator | 85/100 | 🟡 |
| HVAC | 70/100 | 🟡 |
| Equipment Environment | 80/100 | 🟡 |
| Water Systems | 65/100 | 🟠 |
| Electrical | 75/100 | 🟡 |
| Plumbing | 60/100 | 🟠 |
| Waste Management | 90/100 | 🟢 |
| Fire Safety | 55/100 | 🟠 |
| Pest Control | 85/100 | 🟡 |
| Cleanliness | 95/100 | 🟢 |

🔴 CRITICAL ISSUES REQUIRING IMMEDIATE ATTENTION

1. Three fire extinguishers expired (safety compliance violation) - ₦45,000

2. Two toilets with constant running water (wasting ~500L/day = ₦15 - ₦40,000

3. AC Unit 3 making unusual noise (potential imminent failure - emergency replacement would cost ₦200 - ₦30,000

| Critical Repairs (Fix Within 7 Days): | ₦115,000 |
| --- | --- |
| Total All Recommendations: | ₦605,000 |

# DETAILED FINDINGS

## 1. Generator Health

| SCORE | 🟡 85/100 - GOOD |
| --- | --- |

Issues Found:

Oil slightly dark; Battery terminals have minor corrosion

Detailed Notes:

Generator is in good operational condition. Load test passed successfully. Oil level adequate but color indicates it's nearing change interval. Battery voltage at 12.6V which is acceptable. No fuel leaks detected. Exhaust smoke is normal. Generator has been well-maintained overall.

Recommendations:

Oil change - ₦15

## 2. HVAC/AC Systems

| SCORE | 🟡 70/100 - GOOD |
| --- | --- |

Issues Found:

Unit 3 in main ward making rattling noise; Unit 5 in reception cooling inadequately; Filters in 4 units are dirty

Detailed Notes:

Out of 8 AC units

Recommendations:

Service Unit 3 - ₦30

## 3. Medical Equipment Environment

| SCORE | 🟡 80/100 - GOOD |
| --- | --- |

Issues Found:

Temperature slightly elevated in imaging room during peak hours

Detailed Notes:

Medical equipment storage and operating rooms maintain good environmental conditions. Temperature monitoring shows imaging room reaches 28°C during afternoon peak hours

Recommendations:

Install additional ventilation fan in imaging room - ₦40

## 4. Water Systems

| SCORE | 🟠 65/100 - FAIR |
| --- | --- |

Issues Found:

Water pressure low in second floor; External water tank shows rust/corrosion; One tap in staff toilet dripping

Detailed Notes:

Water supply is generally reliable but pressure on second floor is noticeably lower than ground floor. External inspection of overhead tank reveals rust patches on exterior surface which may indicate need for cleaning and maintenance. Small leak in staff toilet tap causing water wastage estimated at 20 liters per day.

Recommendations:

Tank cleaning and exterior treatment - ₦80

## 5. Electrical Systems

| SCORE | 🟡 75/100 - GOOD |
| --- | --- |

Issues Found:

12 burned out bulbs throughout facility; 2 non-functional outlets in storage room; One light switch in pharmacy not working

Detailed Notes:

Electrical infrastructure is generally sound with no exposed wiring detected. Most circuits are functioning properly. The burned out bulbs are concentrated in the corridor (8 bulbs) and patient rooms (4 bulbs). Storage room outlets appear to be a circuit issue rather than individual outlet failure.

Recommendations:

Bulb replacements (12 units) - ₦12

## 6. Plumbing & Drainage

| SCORE | 🟠 60/100 - FAIR |
| --- | --- |

Issues Found:

Toilet in Ward B not flushing properly; Sink drain in laboratory slow; Foul odor from drain in cleaning room; 2 toilets have running water (constant flow)

Detailed Notes:

Plumbing system requires attention in multiple areas. Ward B toilet has weak flush indicating possible valve or water pressure issue. Laboratory sink drains slowly suggesting partial blockage. Cleaning room drain emits sewage odor indicating possible trap issue or main line problem. Two toilets continuously running causing significant water waste (estimated 500 liters per day combined).

Recommendations:

Toilet flush repairs (3 units) - ₦60

## 7. Medical Waste Management

| SCORE | 🟢 90/100 - EXCELLENT |
| --- | --- |

Issues Found:

One yellow bin lid broken in outpatient area

Detailed Notes:

Medical waste management system is exemplary. Proper segregation observed throughout facility. Yellow bins for infectious waste are present in all required locations. Sharp containers are available and not overfilled. Waste storage area is secure and well-maintained. Staff demonstrate good understanding of protocols.

Recommendations:

Replace broken yellow bin lid - ₦8

## 8. Fire Safety

| SCORE | 🟠 55/100 - FAIR |
| --- | --- |

Issues Found:

3 fire extinguishers expired (dates: 2023); Fire extinguisher in pharmacy not accessible (blocked by supplies); Exit sign in back corridor not illuminated; No fire drill conducted in past 12 months

Detailed Notes:

Fire safety infrastructure exists but requires urgent attention. Three extinguishers have expired tags from 2023 and need immediate refilling or replacement. Pharmacy extinguisher is blocked by medical supplies stacked in front of it. Emergency exit signage in back corridor has non-functional lighting. Staff report no fire drills have been conducted recently.

Recommendations:

Refill/replace 3 expired extinguishers - ₦45

## 9. Pest Control

| SCORE | 🟡 85/100 - GOOD |
| --- | --- |

Issues Found:

Minor ant activity observed in staff kitchen area

Detailed Notes:

Facility is generally pest-free. No evidence of rodent activity. No cockroach sightings. Small ants observed in staff kitchen near food storage area but this is minor and easily addressed. Last fumigation was conducted 2 months ago. Food storage areas are properly sealed except staff kitchen.

Recommendations:

Targeted ant treatment in kitchen - ₦15

## 10. Cleanliness & Hygiene

| SCORE | 🟢 95/100 - EXCELLENT |
| --- | --- |

Issues Found:

None significant - facility maintained to high standard

Detailed Notes:

Facility cleanliness is outstanding. Floors are spotless throughout. Patient rooms are well-maintained. Toilets are clean and well-stocked with supplies. Hand sanitizer dispensers are present at all required locations and filled. Staff demonstrates excellent housekeeping practices. Only minor suggestion would be more frequent deep cleaning of corridor corners.

Recommendations:

Continue current excellent cleaning protocols; Consider quarterly deep cleaning of all corners and hard-to-reach areas - ₦50

# RECOMMENDATIONS & NEXT STEPS

Based on this comprehensive facility health assessment, we recommend the following priority actions:

IMMEDIATE (Within 7 Days):

Address all critical issues identified in the Executive Summary to prevent facility disruptions and ensure safety compliance.

SHORT-TERM (Within 30 Days):

Implement all category-specific recommendations to improve overall facility performance and prevent future emergencies.

LONG-TERM (Within 90 Days):

Establish a monthly facility maintenance program to maintain optimal facility health scores and prevent costly emergency repairs.

📅 NEXT HEALTH CHECK SCHEDULED:

We recommend monthly facility health checks to track improvements and identify issues early. Your next inspection is due 30 days from this report date.

📞 CONTACT CYFT CONSULTING Contact: Dr. Amina Mohammed Phone: 080-1234-5678 Email: info@cyftconsulting.com Website: www.cyftconsulting.com