⚡ GENERATOR HEALTH - INSPECTION CHECKLIST

Facility Name: _________________________________________

Inspector Name: _________________________________________

Inspection Date: _________________________________________

Maximum Points for Category: 50

INSTRUCTIONS: For each checkpoint, check ☑ if satisfactory, leave blank ☐ if unsatisfactory. Award points based on percentage of checkpoints passed. Add notes for any issues found.

1. Load Testing Performance (15 points)

☐ Run generator at 100% capacity for 30 minutes

☐ Check voltage output (220-240V ±5%)

☐ Monitor frequency stability (50Hz ±0.5Hz)

☐ Observe for unusual vibrations or sounds

☐ Check exhaust temperature (not exceeding manufacturer spec)

☐ Test automatic load transfer switch operation

Checkpoints Passed: _____ / 6

Points Awarded: _____ / 15

Notes / Issues Found:

_________________________________________________________________

_________________________________________________________________

Estimated Repair Cost (if applicable): ₦_________________

2. Oil Quality and Levels (10 points)

☐ Check oil level using dipstick (between MIN and MAX)

☐ Observe oil color (should be amber, not black)

☐ Check for metal particles in oil

☐ Verify last oil change date (should be <6 months)

☐ Check for oil leaks around engine

☐ Test oil pressure gauge functionality

Checkpoints Passed: _____ / 6

Points Awarded: _____ / 10

Notes / Issues Found:

_________________________________________________________________

_________________________________________________________________

Estimated Repair Cost (if applicable): ₦_________________

3. Battery Condition (10 points)

☐ Check battery voltage (12.6V-13.2V when off, 13.7V-14.7V when charging)

☐ Inspect battery terminals for corrosion (clean if present)

☐ Check electrolyte levels (top up with distilled water if low)

☐ Test battery load capacity

☐ Check battery mounting security

☐ Verify battery date (replace if >3 years old)

Checkpoints Passed: _____ / 6

Points Awarded: _____ / 10

Notes / Issues Found:

_________________________________________________________________

_________________________________________________________________

Estimated Repair Cost (if applicable): ₦_________________

4. Fuel System Inspection (10 points)

☐ Check fuel level in main tank (should be >50%)

☐ Inspect fuel lines for leaks or cracks

☐ Check fuel filter condition (replace if >1 year)

☐ Drain water separator if present

☐ Inspect fuel tank for contamination

☐ Verify fuel quality (clear diesel, no water/sediment)

Checkpoints Passed: _____ / 6

Points Awarded: _____ / 10

Notes / Issues Found:

_________________________________________________________________

_________________________________________________________________

Estimated Repair Cost (if applicable): ₦_________________

5. Maintenance Records Review (5 points)

☐ Verify weekly exercise log (30 min/week minimum)

☐ Check last professional service date (<6 months)

☐ Review any fault codes or warnings

☐ Confirm spare parts availability

☐ Check warranty status

☐ Verify service contract is active

Checkpoints Passed: _____ / 6

Points Awarded: _____ / 5

Notes / Issues Found:

_________________________________________________________________

_________________________________________________________________

Estimated Repair Cost (if applicable): ₦_________________

GENERATOR HEALTH - INSPECTION SUMMARY

| Item | Max Points | Points Awarded |
| --- | --- | --- |
| Load Testing Performance | 15 | ______ |
| Oil Quality and Levels | 10 | ______ |
| Battery Condition | 10 | ______ |
| Fuel System Inspection | 10 | ______ |
| Maintenance Records Review | 5 | ______ |
| TOTAL | 50 | ______ |

Category Score: _____ / 100

Status: ☐ Excellent (90-100)  ☐ Good (70-89)  ☐ Fair (50-69)  ☐ Critical (<50)

OVERALL FINDINGS / RECOMMENDATIONS:

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

Inspector Signature: _______________________________

Date: _______________________________